## cable
Index | ID | FromBus | ToBus | CableLengthUnit | InService | InServiceState | LengthValue | OhmsPerLengthUnit | OhmsPerLengthValue | RPosValue | RZeroValue | XPosValue | XZeroValue | YPosValue | YZeroValue
1 | Cable1 | Bus_市南路1号电缆分接箱 | Bus_草河F27 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
2 | Cable2 | Bus_草河村22号高低开关房 | Bus_市南路1号电缆分接箱 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
3 | Cable3 | Bus_沙龙干01杆 | Bus_草河村22号高低开关房 | 2 | true | As-Built | 500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
4 | Cable4 | Bus_沙龙干03塔开关 | Bus_沙龙干01杆 | 2 | true | As-Built | 2000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
5 | Cable5 | Bus_沙龙干03塔开关 | Bus_13塔 | 2 | true | As-Built | 3000 | 2 | 1000 | 0.230000004 | 0.365999997 | 0.0529999994 | 0.135000005 | 0 | 0
6 | Cable6 | Bus_13塔 | Bus_草河村32号欧式箱变 | 2 | true | As-Built | 1200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
7 | Cable7 | Bus_草河村32号欧式箱变 | Bus_草河F7 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
8 | Cable8 | Bus_桥发支01杆 | Bus_沙龙干03塔开关 | 2 | true | As-Built | 750 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
9 | Cable9 | Bus_桥发支19塔开关 | Bus_桥发支01杆 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
10 | Cable10 | Bus_桥发支19塔开关 | Bus_沙龙干20杆开关 | 2 | true | As-Built | 200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
11 | Cable11 | Bus_沙龙干20杆开关 | Bus_沙龙干33塔开关 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
12 | Cable12 | Bus_沙龙干33塔开关 | Bus_35杆 | 2 | true | As-Built | 400 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
13 | Cable13 | Bus_35杆 | Bus_沙龙干44塔开关 | 2 | true | As-Built | 1080 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
14 | Cable14 | Bus_大刀沙支01杆 | Bus_沙龙干20杆开关 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
15 | Cable59 | Bus_大刀沙水厂_中压 | Bus_大刀沙支01杆 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
16 | Cable15 | Bus_10塔 | Bus_大刀沙水厂_中压 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
17 | Cable16 | Bus_11杆 | Bus_10塔 | 2 | true | As-Built | 1600 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
18 | Cable62 | Bus_大刀沙支18杆 | Bus_11杆 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
19 | Cable63 | Bus_大刀沙村5号 | Bus_大刀沙支18杆 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
20 | Cable72 | Bus_大刀沙村3号 | Bus_11杆 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
21 | Cable65 | Bus_大刀沙村2号 | Bus_大刀沙支30杆 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
22 | Cable64 | Bus_大刀沙支30杆 | Bus_大刀沙支28+1杆 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
23 | Cable17 | Bus_大刀沙支28+1杆 | Bus_大刀沙支18杆 | 2 | true | As-Built | 2100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
24 | Cable66 | Bus_大刀沙支42杆 | Bus_大刀沙支30杆 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
25 | Cable67 | Bus_大刀沙村合作经济社 | Bus_大刀沙支42杆 | 2 | true | As-Built | 1080 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
26 | Cable68 | Bus_大刀沙支53杆 | Bus_大刀沙支42杆 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
27 | Cable69 | Bus_大刀沙村1号 | Bus_大刀沙支53杆 | 2 | true | As-Built | 1000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
28 | Cable70 | Bus_大刀沙支64杆 | Bus_大刀沙支53杆 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
29 | Cable61 | Bus_大刀沙村4号 | Bus_大刀沙支64杆 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.0270000007 | 0 | 0
30 | Cable71 | Bus_76杆 | Bus_大刀沙支64杆 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
31 | Cable20 | Bus_大刀沙支77塔 | Bus_76杆 | 2 | true | As-Built | 120 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
32 | Cable21 | Bus_大刀沙支77塔 | Bus_01塔 | 2 | true | As-Built | 2000 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
33 | Cable22 | Bus_01塔 | Bus_观龙大站高低压开关房 | 2 | true | As-Built | 1320 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
34 | Cable23 | Bus_观龙大站高低压开关房 | Bus_观龙大站2号高低压开关房 | 2 | true | As-Built | 1650 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
35 | Cable24 | Bus_观龙大站2号高低压开关房 | Bus_观龙大站支01杆 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
36 | Cable25 | Bus_06杆 | Bus_观龙大站支01杆 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
37 | Cable26 | Bus_观龙大站支01杆 | Bus_03杆 | 2 | true | As-Built | 950 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
38 | Cable27 | Bus_03杆 | Bus_清流观龙18队 | 2 | true | As-Built | 1800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
39 | Cable58 | Bus_观龙大站2号高低压开关房 | Bus_52杆 | 2 | false | As-Built | 2500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
40 | Cable56 | Bus_52杆 | Bus_30杆 | 2 | true | As-Built | 1600 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
41 | Cable55 | Bus_30杆 | Bus_21杆 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
42 | Cable54 | Bus_21杆 | Bus_清流干19杆开关 | 2 | true | As-Built | 1400 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
43 | Cable53 | Bus_清流干19杆开关 | Bus_清流干08塔 | 2 | true | As-Built | 950 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
44 | Cable52 | Bus_清流干08塔 | Bus_南清干45塔与清流干01 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
45 | Cable50 | Bus_南清干45塔与清流干01 | Bus_28杆 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.0900000036 | 0 | 0
46 | Cable43 | Bus_28杆 | Bus_南清干27塔开关 | 2 | true | As-Built | 190 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
47 | Cable42 | Bus_南清干27塔开关 | Bus_26塔 | 2 | true | As-Built | 1100 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
48 | Cable41 | Bus_26塔 | Bus_清流1号电缆分接箱 | 2 | true | As-Built | 1160 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
49 | Cable39 | Bus_清流1号电缆分接箱 | Bus_清流1号支16杆 | 2 | false | As-Built | 450 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
50 | Cable37 | Bus_南清干24杆开关 | Bus_清流1号支16杆 | 2 | false | As-Built | 1405 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
51 | Cable36 | Bus_南清干14杆开关 | Bus_南清干24杆开关 | 2 | false | As-Built | 970 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.0900000036 | 0 | 0
52 | Cable35 | Bus_裕丰13塔 | Bus_南清干14杆开关 | 2 | false | As-Built | 1180 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
53 | Cable34 | Bus_08塔 | Bus_裕丰13塔 | 2 | false | As-Built | 1200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
54 | Cable33 | Bus_南清干04塔开关 | Bus_08塔 | 2 | false | As-Built | 1360 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
55 | Cable32 | Bus_02塔 | Bus_南清干04塔开关 | 2 | false | As-Built | 1400 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
56 | Cable31 | Bus_南清干01杆 | Bus_02塔 | 2 | false | As-Built | 1130 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
57 | Cable30 | Bus_南派1号电缆分接箱 | Bus_南清干01杆 | 2 | false | As-Built | 1360 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
58 | Cable29 | Bus_清河东路电缆分接箱 | Bus_南派1号电缆分接箱 | 2 | false | As-Built | 900 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
59 | Cable28 | Bus_石楼F12 | Bus_清河东路电缆分接箱 | 2 | false | As-Built | 1700 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
60 | Cable38 | Bus_裕丰13塔 | Bus_裕丰F19 | 2 | false | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
61 | Cable40 | Bus_清流1号电缆分接箱 | Bus_南清干24杆开关 | 2 | false | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
62 | Cable51 | Bus_京毅开关房 | Bus_南清干45塔与清流干01 | 2 | true | As-Built | 1450 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
63 | Cable49 | Bus_信强贸易开关 | Bus_京毅开关房 | 2 | true | As-Built | 1150 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
64 | Cable45 | Bus_清流村经济合作社开关房 | Bus_信强贸易开关 | 2 | true | As-Built | 1350 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
65 | Cable44 | Bus_石楼F22 | Bus_清流村经济合作社开关房 | 2 | true | As-Built | 200 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
66 | Cable46 | Bus_信强贸易开关 | Bus_八糖尾鱼塘支01杆 | 2 | true | As-Built | 1500 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
67 | Cable47 | Bus_八糖尾鱼塘支01杆 | Bus_28塔 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
68 | Cable48 | Bus_28塔 | Bus_八糖鱼45杆 | 2 | true | As-Built | 1600 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
69 | Cable57 | Bus_清流村会堂2号高低压开关 | Bus_30杆 | 2 | true | As-Built | 1300 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
70 | Cable60 | Bus_大刀沙水厂_交流 | Bus_大刀沙水厂_中压 | 2 | true | As-Built | 800 | 2 | 1000 | 0.0599999987 | 0.0599999987 | 0.0900000036 | 0.270000011 | 0 | 0
71 | Cable18 |  |  | 0 | true | As-Built | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
72 | Cable19 |  |  | 0 | true | As-Built | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0

## xline
Index | ID | ExtRef | FixedLoc | OtiGUID | CloneGuid | UseElementColor | Hidden | MetafileName | Orientation | SymbolSize | SymbolType | ServiceState | InheritedState | FromBus | ToBus | ID | IID | InService | InServiceState | Length | LengthUnit | PerLength | PerLengthUnit | RPos | RZero | XPos | XZero | YPos | YZero

## bus
Index | ID | OpVMag | OpVAng | UserDefinedPDGUID | InService | ServiceState | Area | AsymmRMS | BasekV | BusReferenceName | NominalkV | VMag | VMaxLimit | VMinLimit | Zone
1 | Bus_草河F27 | 99.999984741 | 1.6574085748e-05 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
2 | Bus_市南路1号电缆分接箱 | 99.7008667 | 0.0444202386 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
3 | Bus_草河村22号高低开关房 | 99.4018173 | 0.0890911147 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
4 | Bus_沙龙干01杆 | 99.3546066 | 0.0733531639 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
5 | Bus_沙龙干03塔开关 | 98.9588852 | 0.123386197 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
6 | Bus_13塔 | 98.8585281 | 0.143181458 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
7 | Bus_草河村32号欧式箱变 | 98.8465729 | 0.14002277 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
8 | Bus_草河F7 | 98.8465729 | 0.14002277 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
9 | Bus_桥发支01杆 | 98.9109879 | 0.105756074 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
10 | Bus_桥发支19塔开关 | 98.8481369 | 0.0824859813 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
11 | Bus_沙龙干20杆开关 | 98.8355637 | 0.0778284147 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
12 | Bus_沙龙干33塔开关 | 98.7944641 | 0.0669621602 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
13 | Bus_35杆 | 98.7838974 | 0.0641684011 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
14 | Bus_沙龙干44塔开关 | 98.7564545 | 0.0569071062 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
15 | Bus_大刀沙支01杆 | 98.8150787 | 0.0657259747 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
16 | Bus_大刀沙水厂_中压 | 98.7884445 | 0.049985297 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
17 | Bus_10塔 | 98.7670059 | 0.0369497687 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
18 | Bus_11杆 | 98.7374268 | 0.0184012167 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
19 | Bus_大刀沙支18杆 | 98.6889191 | 0.00562515762 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
20 | Bus_大刀沙村5号 | 98.6889191 | 0.00562515762 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
21 | Bus_大刀沙村3号 | 98.7829819 | 0.0236881208 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
22 | Bus_大刀沙村2号 | 98.5522385 | -0.0304477587 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
23 | Bus_大刀沙支30杆 | 98.5522385 | -0.0304477587 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
24 | Bus_大刀沙支28+1杆 | 98.5963287 | -0.0188004058 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
25 | Bus_大刀沙支42杆 | 98.4861145 | -0.0479383357 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
26 | Bus_大刀沙村合作经济社 | 98.4850388 | -0.0482247435 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
27 | Bus_大刀沙支53杆 | 98.4215012 | -0.0650541112 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
28 | Bus_大刀沙村1号 | 98.4205017 | -0.0653196424 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
29 | Bus_大刀沙支64杆 | 98.3752213 | -0.0773275942 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
30 | Bus_大刀沙村4号 | 98.3730164 | -0.0779123381 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
31 | Bus_76杆 | 98.3431702 | -0.0858354867 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
32 | Bus_大刀沙支77塔 | 98.3383636 | -0.0871121436 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
33 | Bus_01塔 | 98.2982559 | -0.0977558568 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
34 | Bus_观龙大站高低压开关房 | 98.2731171 | -0.104433887 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
35 | Bus_观龙大站2号高低压开关房 | 98.2433395 | -0.112346508 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
36 | Bus_观龙大站支01杆 | 98.2245941 | -0.117330991 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
37 | Bus_06杆 | 98.2245941 | -0.117330991 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
38 | Bus_03杆 | 98.2084045 | -0.1216373 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
39 | Bus_清流观龙18队 | 98.1777344 | -0.129800513 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
40 | Bus_52杆 | 97.8954315 | -0.1614317 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
41 | Bus_30杆 | 97.8793335 | -0.165726751 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
42 | Bus_21杆 | 97.8671112 | -0.168989241 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
43 | Bus_清流干19杆开关 | 97.8558426 | -0.171997368 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
44 | Bus_清流干08塔 | 97.8482056 | -0.174038991 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
45 | Bus_南清干45塔与清流干01 | 97.8386993 | -0.17657803 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
46 | Bus_28杆 | 97.8370895 | -0.177007973 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
47 | Bus_南清干27塔开关 | 97.8368912 | -0.177059039 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
48 | Bus_26塔 | 97.8357925 | -0.177354619 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
49 | Bus_清流1号电缆分接箱 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
50 | Bus_清流1号支16杆 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
51 | Bus_南清干24杆开关 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
52 | Bus_南清干14杆开关 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
53 | Bus_裕丰13塔 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
54 | Bus_08塔 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
55 | Bus_南清干04塔开关 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
56 | Bus_02塔 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
57 | Bus_南清干01杆 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
58 | Bus_南派1号电缆分接箱 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
59 | Bus_清河东路电缆分接箱 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
60 | Bus_石楼F12 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
61 | Bus_裕丰F19 | 0 | 0 |  | false | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
62 | Bus_京毅开关房 | 97.831398 | -0.178526312 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
63 | Bus_信强贸易开关 | 97.8267746 | -0.179762617 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
64 | Bus_清流村经济合作社开关房 | 97.8254166 | -0.18012546 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
65 | Bus_石楼F22 | 97.8254166 | -0.18012546 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
66 | Bus_八糖尾鱼塘支01杆 | 97.823761 | -0.180568963 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
67 | Bus_28塔 | 97.8211365 | -0.181267828 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
68 | Bus_八糖鱼45杆 | 97.8195267 | -0.18169792 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
69 | Bus_清流村会堂2号高低压开关 | 97.8780289 | -0.166075781 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
70 | Bus_大刀沙水厂_交流 | 98.7876434 | 0.0497744456 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
71 | Bus1 | 0 | 0 |  | true | 1 | 1 | 0 | 0 | 0 | 0 | 100 | 105 | 90 | 1
72 | Bus_45杆 | 0 | 0 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1
73 | Bus2 | 0 | 0 |  | true | 1 | 1 | 0 | 0 | 0 | 10 | 100 | 105 | 90 | 1

## xform2w
Index | ID | AnsiMaxMVA | AnsiMVA | AnsiPosXR | AnsiPosZ | AnsiZeroXoverR | AnsiZeroZ | Buried | VectorOrWinding | PrimConnectionButton | SecConnectionButton | PrimNeutralConn | SecNeutralConn | CenterTap | PrimPercentTap | SecPercentTap | PrimMaxPercentFixedTap | PrimMinPercentFixedTap | SecMaxPercentFixedTap | SecMinPercentFixedTap | PhaseShiftHL | PhaseShiftPS | PhaseShiftType | FromBus | ToBus | InService | InServiceState | PrimkV | SeckV | ZBaseMVA

## xform3w
Index | ID | InService | InServiceState | PrimaryBus | SecondaryBus | TeritiaryBus | PrimkV | SeckV | TerkV | PrimPercentTap | SecPercentTap | TerPercentTap | PrimkVA | SeckVA | TerkVA | PSPosZ | PSPosXoverR | PTPosZ | PTPosXoverR | STPosZ | STZeroXoverR

## util
Index | ID | OpVAng | OpVMag | OpMW | OpMvar | VoltagePercent0 | VoltagePercent1 | VoltagePercent2 | VoltagePercent3 | VoltagePercent4 | VoltagePercent5 | VoltagePercent6 | VoltagePercent7 | VoltagePercent8 | VoltagePercent9 | BalancedRadio | Bus | EarthingType | GroundingConnection | InService | InServiceState | kAsc1p | kAsc3p | KV | MaxQ | MinQ | Mvar | MW | NegR | NegX | OnePhase | OnePhaseXoverR | Phase | PhaseType | PosR | PosX | ThreePhase | ThreePhaseXoverR | TypeOfUtility | VoltageAngle | VoltageMagnitude | ZeroR | ZeroX | PdeStatus
1 | U2 | 0 | 100 | 170.21965 | 105.686005 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | Bus_石楼F12 | 0 | 0 | false | As-Built | 40.8248291 | 40.8248291 | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 707106.812 | 1 | 0 | 5 | 10 | 10 | 707106.812 | 1 | 0 | 0 | 100 | 10 | 10 | Swing
2 | U1 | 0 | 100 | 178.979691 | 110.86953 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | Bus_草河F27 | 0 | 0 | true | As-Built | 40.8248291 | 40.8248291 | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 707106.812 | 1 | 0 | 5 | 10 | 10 | 707106.812 | 1 | 0 | 0 | 100 | 10 | 10 | Swing

## syngen
Index | ID | Bus | CalcFromCapability | CompoundExc | CouplerRpm | CouplerWR2 | Damping | Efficency | Eqp | ExcWithstandLimit | ExcWithstandTime | GenerationCategory | GostScExciterType | IecExcitationType | Ikp | IncludePFMvarController | Inertia | InService | InServiceState | KV | LoadRpm | LoadWR2 | MachineType | MachineWR2 | MVA | MW | PG | PlotI2t | PlotShortTime | Poles | PowerFactor | PrimConnectionButton | PrimEarthingType | PrimGroundingType | PrimNeutralConn | RadioButtons | RatedLifeTime | RdcPercent | ReactivePower | RealPower | RPM | S100 | S120 | Sbreak | ScExciterType | ScGenType | TDoublePrimeD0 | TDoublePrimeQ0 | TPrimeD0 | TPrimeQ0 | TypeOfGenerator | VoltageAngle | VoltageMagnitude | X0 | X1 | X2 | Xd | XdDoublePrime | XdPrime | XOverR | XOverR0 | XOverR2 | Xq | XqDoublePrime | XqPrime | XTolerance | PdeStatus

## pvarray
Index | ID | Bus | BVmpp | BVmppTemp | AIscTemp | InverterIncluded | BVoc | BVocTemp | DCGrounded | DCGroundR | DeltaIrradiance | EarthingType | ExternalL | ExternalR | GenerationCategory | Impp | ImpUD | InService | InServiceState | InverterIncluded | Isc | IscUD | Issue | LibModified | MppTracker | NOCTemp | NumPanelParallel | NumPanelSeries | PhaseType | PVAPower | PVAPowerTol | RevCtrl | Revision | SCModel | ValidEquipmentCable | Vmpp | VmpUD | Voc | VocUD | OutServiceYear | ProfileSector | PVAMFR | PVAModel | PVANumCells | PVASize | PVAType | PVAVDC | SingleYearForecastOpt | UniformScalePQ | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime
1 | PVA1 | Bus_大刀沙村5号直流 | 0 | 0 | 0.0548 | 0 | 0 | -0.362399995 | 0 | 0 | 0.0500000007 | 5 | 0 | 0 | EP8AAPD/AAAKAAAA6AMAAAAAyEEBAHtCk2qURIQDAAAAAPBBZ+Z/Qt3OgkQgAwAAAADwQc3McEI3JWdEvAIAAAAA8EE0s2FCctxIRFgCAAAAAPBBmplSQkvKKkT0AQAAAADwQQCAQ0Lv9wxEkAEAAAAA8EFmZjRClOTeQywBAAAAAPBBzUwlQtGZpEPIAAAAAADwQTMzFkLwo1ZDZAAAAAAA8EGaGQdCTWPOQg | 7.30000019 | 0 | true | As-Built | 0 | 7.96000004 | 0 | 0 | 0 | 0 | 50.2000008 | 200 | 27 | 0 | 219.876007 | 0 | 0 | 0 | 0 | 0 | 30.1200008 | 0 | 36.0600014 | 0 | 2045/1/1 |  | A10Green Technology | A10J-M60-220 | 60 | 220 | Polycrystalline | 1 | 0 | 1 | 0.0030000000000000001 | 200 | 0 | 0.000136970004 | 43.7999992 | 0.0030000000000000001 | 10 | 0 | 200

## lumpedload
Index | ID | OpMW | OpMvar | OpMWStLd | OpMvarStLd | GroundingAmp | GroundingOhm | GroundingType | Bus | InService | InServiceState | KV | LRC | ModelType | MotorLoadPercent | MTLoadPercent | MVA | NeutralConn | PercentTotalLoad | PF | Phase | PhaseA_MVA | PhaseB_MVA | PhaseC_MVA | PhaseConnection | StaticLoadPercent | TdP | X | XdP | XOverR | XP | XPP | PdeStatus | BasekV | LoadType | OutServiceYear | PhaseA_Amp | PhaseA_PF | PhaseB_Amp | PhaseB_PF | PhaseC_Amp | PhaseC_PF | Priority | ProfileSector | SingleYearForecastOpt | Ta | UDBasekV | UniformScalePQ | WR | DataStream | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime
1 | Lump35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_草河村32号欧式箱变 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 100 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
2 | Lump3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_13塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 48 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
3 | Lump37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_沙龙干44塔开关 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 255 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
4 | Lump6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_35杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
5 | Lump5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_沙龙干33塔开关 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
6 | Lump42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_大刀沙村合作经济社 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
7 | Lump40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_大刀沙村1号 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
8 | Lump36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_大刀沙村4号 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 20 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
9 | Lump14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清流观龙18队 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 170 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
10 | Lump34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清河东路电缆分接箱 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
11 | Lump33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_南派1号电缆分接箱 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
12 | Lump32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_南清干01杆 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
13 | Lump31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_02塔 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
14 | Lump30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_南清干04塔开关 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
15 | Lump29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_08塔 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
16 | Lump28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_南清干14杆开关 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
17 | Lump27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清流1号支16杆 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
18 | Lump26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清流1号电缆分接箱 | false | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
19 | Lump25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_26塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
20 | Lump24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_28杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
21 | Lump21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清流村经济合作社开关房 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
22 | Lump23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_八糖鱼45杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
23 | Lump22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_28塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
24 | Lump20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_信强贸易开关 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
25 | Lump19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_京毅开关房 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
26 | Lump18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清流干08塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
27 | Lump17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_21杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
28 | Lump15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_清流村会堂2号高低压开关 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
29 | Lump16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_52杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
30 | Lump13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_观龙大站2号高低压开关房 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
31 | Lump12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_观龙大站高低压开关房 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
32 | Lump11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_01塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
33 | Lump10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_大刀沙支77塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 200 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
34 | Lump8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_11杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 200 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
35 | Lump7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_10塔 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 200 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
36 | Lump38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_大刀沙水厂_交流 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
37 | Lump39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_沙龙干20杆开关 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 150 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
38 | Lump4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_桥发支01杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
39 | Lump41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_沙龙干03塔开关 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
40 | Lump2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_沙龙干01杆 | true | As-Built | 10 | 650 | Conventional | 80 | 100 | 150 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
41 | Lump1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus_草河村22号高低开关房 | true | As-Built | 10 | 600 | Conventional | 80 | 100 | 300 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 50 | 6.67000008 | 25 | 16.666666 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50
42 | Lump9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | true | As-Built | 10 | 650 | Conventional | 80 | 80 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 0.200000003 | 150 | 23.0769234 | 6.67000008 | 23.0769234 | 15.3846149 | Continuous | 0 | 0 | 2045/1/1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 0 | 0 | 1 | 0 | EP8AAAIAAAD//v8A//7/AP/+/wD//v8A//7/AAAAAAAAAAAA | 0 | 50 | 1 | 0.150000006 | 50 | 0.019999999552965199 | 10 | 0 | 50

## capacitor
Index | ID | OpMW | OpMvar | InService | InServiceState | InterDF | Phase | PhaseConnection | PdeStatus | CurrentLowerBand | CurrentSwitchInValue | CurrentSwitchOutValue | CurrentUpperBand | StepsPerBank | TimeDelayType | VoltageCtrlUnit | VoltageLowerBand | VoltageSwitchInValue | VoltageSwitchOutValue | VoltageUpperBand | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength

## mgset
Index | ID | KV | MVA | X1 | Xdu | Xq | XqP | XqPP | Xqu | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength

## hvcb
Index | ID | FromElement | ToElement | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | PdeStatus | ReplaceTime | SpareAvail | SwitchTime

## dcbus
Index | ID | InService | InServiceState | MaxLoadFactor | MinLoadFactor | NominalV | PhaseType | WireType | aCoefficient | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength
1 | Bus_大刀沙村5号直流 | true | As-Built | 125 | 80 | 824 | 0 | 1 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Bus_大刀沙村3号直流 | true | As-Built | 125 | 80 | 824 | 0 | 1 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Bus_大刀沙村2号直流 | true | As-Built | 125 | 80 | 824 | 0 | 1 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## dcimpedance
Index | ID | FromBus | IID | InService | InServiceState | RValue | LValue | ToBus | PhaseType | WireType | FailureRate | MomentaryRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UnitLength
1 | dcZ1 | Bus_大刀沙村5号直流 | 3222 | true | As-Built | 0.0599999987 | 0 | Bus_大刀沙村3号直流 | 0 | 1 | 0 | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | dcZ2 | Bus_大刀沙村2号直流 | 3234 | true | As-Built | 0.0599999987 | 0 | Bus_大刀沙村5号直流 | 0 | 1 | 0 | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## dclumpload
Index | ID | DCV | InService | InServiceState | KFactor | KW | MTLoadPercent | Bus | StaticLoadPercent | PhaseType | ProfileSector | SingleYearForecastOpt | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UniformScalePQ

## dcconverter
Index | ID | IMaxPercent | InputBus | InputPhaseType | InputTerminalType | InputV | InService | InServiceState | KW | OutputBus | OutputPhaseType | OutputTap | OutputTerminalType | OutputV | PercentEFF | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime

## dccb
Index | ID | FromBus | ToBus | FailureRate | MTTR | OutageRate | OutageTime | PdeStatus | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime

## inverter
Index | ID | OpAcKw | OpAcKvar | OpAcKv | OpAcAmp | OpDcKw | DckW | DcPercentEFF | DcPercentIMax | DcPhaseType | DcTerminalType | DcV | DcVMax | DcVMin | diDV | EarthingType | GenerationCategory | BusID | CZNetwork | IkPFMax | IkPFMin | IMin | InService | ParentName | InServiceState | KV | GenCat0ACkW | GenCat0kVar | ACOperationMode | KVA | KVAMax | KvarMax | KWMax | MaxPF | MinPF | MPPTControl | MPPTDCVMax | MPPTDCVMin | MPPTInitialDCV | MPPTNumSteps | MvarLimitsOpt | NegSeqCurrentInjection | NegSeqCurrentLimit | NegSeqDeadbandMin | NegSeqDiDV | PF | Phase | PhaseConnection | PowerFactorOpt | RegulatedVac | SmartInverterOpt | SP3Wire | SpareDF | StaticVarSupportPercentage | VAtIMax | VMaxOp | VMinOp | Vref | VShutOff | PdeStatus | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | UserDefPoints
1 | Inv2 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 105 | 0 | 1 | 824 | 110 | 0 | 2 | 0 | IP8AAPP/AAAKAAAAAADIQgAAyEIAAAAAAADIQgAAAAAAAEhCAADIQgAAAAAAAAAAAAAAAAAAoEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAADAAAAAAAAAAAAVkAAAAAAAABZQAAAAAAAAFZAAAAAAAAAWUAAAAAAAIBaQAAAAAAAAFlAAAAAAACAWkAAAAAAAABZQAAAAAAAgFtAAAAAAAAANEAAAAAAAIBbQAAAAAAAADRAAAAAAA | Bus_大刀沙村5号 | Bus_大刀沙村5号直流 | 110 | 100 | 100 | false |  | As-Built | 10 | 100 | 50 | Smart Inverter Control | 0 | 300 | 0 | 0 | 100 | 80 | 0 | 110 | 40 | 100 | 15 | 0 | 0 | 100 | 10 | 2 | 100 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 40 | 110 | 90 | 100 | 50 | Continuous | 1.254 | 5 | 1 | 8 | 1.254 | 10 | 0 | 2 | <UserDefPoints><UserDefPQPoints></UserDefPQPoints><UserDefPVPoints><UserDefPVPoint percentVGenerating="88.00" percentPGenerating="100.00" percentVCharging="88.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="106.00" percentPGenerating="100.00" percentVCharging="106.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="110.00" percentPGenerating="20.00" percentVCharging="110.00" percentPCharging="20.00" /></UserDefPVPoints><UserDefQVPoints></UserDefQVPoints></UserDefPoints>
2 | Inv1 | 0 | 0 | 0 | 0 | 0 | 3000 | 90 | 105 | 0 | 1 | 824 | 110 | 0 | 2 | 5 | IP8AAPP/AAAKAAAAAADIQgAAlkMAAAAAAADIQgAAAAAAAJZDAADIQgAAAAAAAAAAAAAAAAAAoEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAADAAAAAAAAAAAAVkAAAAAAAABZQAAAAAAAAFZAAAAAAAAAWUAAAAAAAIBaQAAAAAAAAFlAAAAAAACAWkAAAAAAAABZQAAAAAAAgFtAAAAAAAAANEAAAAAAAIBbQAAAAAAAADRAAAAAAA | Bus_大刀沙村3号 | Bus_大刀沙村3号直流 | 110 | 100 | 100 | true |  | As-Built | 10 | 300 | 300 | Smart Inverter Control | 2700 | 2700 | 2700 | 2700 | 100 | 80 | 0 | 110 | 40 | 100 | 15 | 0 | 0 | 100 | 10 | 2 | 100 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 40 | 110 | 90 | 100 | 50 | Continuous | 1.254 | 5 | 1 | 8 | 1.254 | 10 | 0 | 2 | <UserDefPoints><UserDefPQPoints></UserDefPQPoints><UserDefPVPoints><UserDefPVPoint percentVGenerating="88.00" percentPGenerating="100.00" percentVCharging="88.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="106.00" percentPGenerating="100.00" percentVCharging="106.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="110.00" percentPGenerating="20.00" percentVCharging="110.00" percentPCharging="20.00" /></UserDefPVPoints><UserDefQVPoints></UserDefQVPoints></UserDefPoints>
3 | Inv3 | 0 | 0 | 0 | 0 | 0 | 300 | 90 | 105 | 0 | 1 | 824 | 110 | 0 | 2 | 5 | IP8AAPP/AAAKAAAAAADIQgAAyEIAAAAAAADIQgAAAAAAAEhCAADIQgAAAAAAAAAAAAAAAAAAoEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAyEIAAAAAAAAAAAAAyEIAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAMhCAAAAAAAAAAAAAMhCAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAAADIQgAAAAAAAAAAAADIQgAAAAAAAAAAAAAAAAAAAAADAAAAAAAAAAAAVkAAAAAAAABZQAAAAAAAAFZAAAAAAAAAWUAAAAAAAIBaQAAAAAAAAFlAAAAAAACAWkAAAAAAAABZQAAAAAAAgFtAAAAAAAAANEAAAAAAAIBbQAAAAAAAADRAAAAAAA | Bus_大刀沙村2号 | Bus_大刀沙村2号直流 | 110 | 100 | 100 | false |  | As-Built | 10 | 100 | 50 | Smart Inverter Control | 270 | 270 | 270 | 270 | 100 | 80 | 0 | 110 | 40 | 100 | 15 | 0 | 0 | 100 | 10 | 2 | 100 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 40 | 110 | 90 | 100 | 50 | Continuous | 1.254 | 5 | 1 | 8 | 1.254 | 10 | 0 | 2 | <UserDefPoints><UserDefPQPoints></UserDefPQPoints><UserDefPVPoints><UserDefPVPoint percentVGenerating="88.00" percentPGenerating="100.00" percentVCharging="88.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="106.00" percentPGenerating="100.00" percentVCharging="106.00" percentPCharging="100.00" /><UserDefPVPoint percentVGenerating="110.00" percentPGenerating="20.00" percentVCharging="110.00" percentPCharging="20.00" /></UserDefPVPoints><UserDefQVPoints></UserDefQVPoints></UserDefPoints>

## charger
Index | ID | OpMW | OpMvar | DckW | DcLoadkW | DcPercentIMax | DcPhaseType | DcSmoothL | DcSmoothR | DcTapPercentage | DcTerminalType | DcV | DcVeq | DcVFloat | DcVFloatMax | DcVFloatMin | IAtZeroV | IMin | InService | InServiceState | Iop | Issue | KV | KVA | MVA | Bus | CZNetwork | MVASc | OperatingAlfa | PercentDF | PercentEFF | Phase | PhaseConnection | ScContribution | ScK | SP3Wire | SpareDF | SystemR | SystemX | SystemXOverR | UpdateZFromSc | VAtIMax | Xc | XfmrR | XfmrX | PdeStatus | ProfileSector | RectifierMaxV | SCMaxV | SCMfrModelID | SCParameter | SCSpeed | SCStandard | FailureRate | MTTR | NoOfLoads | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime

## battery
Index | ID | BatteryType | DisChargeMethod | Eff | IchargeMax | IdischargeMax | InService | InServiceState | Bus | NrOfCells | NoOfPacks | NrOfStrings | IValue | OperatingSoC | OpGenBusGID | OpGenBusID | OpGenChargeBand | OpGenChargeMW | OpGenDisChargeBand | OpGenDisChargeMW | PhaseType | QValue | Rated | TerminalType | VbatMax | VbatMin | FailureRate | MTTR | OutageRate | OutageTime | PermFailureRate | ReplaceTime | SpareAvail | SwitchTime | ModelID | ModelType
1 | Battery1 | 0 | 1 | 85 | 10 | 20 | true | As-Built | Bus_大刀沙村2号直流 | 20 | 20 | 20 | 0 | 100 | 2185560065 | 3220 | 0.00100000005 | 1 | 0.00100000005 | 0.100000001 | 0 | 110 | 3 | 1 | 120 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450043002D003200300030003700200020002000200020000000000000003041443730333430762F000030304330373934343030303030303030190008000000 | 050000000000484300005C4366463B440000CE440AD7233B